|  | ......................... Pc. .............................. € .............................. € GEZE F 1200+ System Drive system for inward opening turn-and-tilt / bottom-hung windows for daily ventilation and exhaust. Drive system consisting of a drive unit, the F 1200+ and the F 1200 turn-and-tilt hardware. Automated tilted position to opening width of 180 mm without chain and manual opening in turning position. In disconnected mode, mechanical emergency locking and unlocking is possible. Drive with integrated operating element and handle function for motorisation of the associated hardware. The number of horizontal/vertical central locking systems depends on the closing force of the leaf. Application Leaf dimensions: ........ mm width (min. 750 mm – max. 2400 mm) ........ mm height (with vertical operation by F 1200+ min.980 mm – max. 3500 mm) (with horizontal operation by F 1200+ 750 mm – max. 3500 mm) Opening width with tilt opening: 180 mm Leaf weight: max. 200 kg (corresponding application diagram can be found in the installation drawing |
| --- | --- |
|  | ......................... Pc. .............................. € .............................. € GEZE F 1200 turn-and-tilt hardware Turn-and-tilt hardware Cranked turn-and-tilt hardware for convenient and simple operation of large and heavy aluminium windows. The hardware consists of a surface-mounted hinge side and a concealed central locking mechanism. Hardware properties Usable in aluminium profile systems Schüco, Hueck, Wicona with the following hardware chamber dimensions: Leaf groove: 21 mm Frame groove: 14 mm Groove depth push rod: 6.5 mm Rebate space: 16 mm Hardware design Colour hinge side: ( ) EV1 / ( ) according to RAL Type of installation / installation position: ( ) DIN R / ( ) DIN L |
|  | ......................... Pc. .............................. € .............................. € GEZE F 1200+ drive Ventilation drive for automation of inward opening turn-and-tilt and bottom-hung windows. Usable only with F 1200 hardware Functions: Electrical locking and unlocking of the hardware in real time with manual turn function plus motorised tilt ventilation for the ventilation mode of tilt and turn and bottom-hung windows with variable adjustment. The high quality aluminium drive unit serves as an ergonomic handle element with manual operation in the turning position. Use of the turning position can either be completely deactivated, or enabled for authorised persons only. Automatic mode enables extremely quiet-running operation. Operating unit with capacitive control keys with LED backlight enables intuitive operation with recommended actions and so prevents misuse by the user. An LED status display shows the opening indication, the operating mode as well as warnings in the event of misuse. Precise control of the operating field by means of proximity sensor to identify when the user is approaching or moving away, and brightness sensor to adjust the ambient brightness. In disconnected mode, the drive can be moved by means of mechanical emergency unlocking. Application Designed for the GEZE F 1200 tilt and turn hardware for leaf heights up to 3.5 m with a maximum leaf weight of up to 200 k (note special groove geometry and application diagrams for the hardware). Opening width with tilt opening: 180 mm Activation Manual operation via integrated operating field on the drive and integration in the building automation in conjunction with GEZE IQ box KNX possible. Installation The drive unit can be installed both vertically and horizontally. A cable transition from the frame to the leaf can be designed as divisible line transition. Pinch protection Up to protection class 3 according to the Machinery Directive EC/42/2006 without additional sensors thanks to reduced closing speed. In conjunction with the GEZE IQ box Safety and suitable sensors, protection class 4 is possible (according to safety analysis). Technical data Supply voltage: 24 V DC / ± 10 % Current consumption: max. 2.5 A Duty rating: ED 30 % Power consumption: 60 W Ambient temperature: -5 °C to +70 °C Unlocking time: < 4s Sound pressure level: < 38 dbA (automatic mode) Speed (tilt) automatic operation 11 mm/s on main closing edge Speed (tilt) manual up to 32 mm/s on main closing edge Housing IP rating: IP 40 Housing: aluminium Dimensions: 506 x 53 x 45 mm (W x H x D) Installation position: ( ) vertical / ( ) horizontal Surface: anodised EV1 Colour: ( ) EV1 / ( ) according to RAL.......... Side cap: ( ) RAL 7012 / ( ) according to RAL.......... Version Type of installation / installation position: ( ) DIN R / ( ) DIN L Turn function: ( ) enabled ( ) mechanical turn block (key) ( ) software-controlled turn block |
|  | ......................... Pc. .............................. € .............................. € Cable transition Concealed cable transition in the rebate space for power supply of the window drives. Cable transition with detachable connection. Application To provide power supply to drives that are mounted on the window leaf Leaf and frame installation Version ( ) Cable transition 4 m / 6 m ( ) Cable transition 2 m / 3 m |
|  | ......................... Pc. .............................. € .............................. € Power supply – NT 6.25 A – 24 V HS power supply Power supply for top hat rail mounting and to supply 24 V drives and control units. Technical data Output voltage: 24 V DC Operating voltage: 230 V +/- 10% Output current: max. 6.25 A IP rating: IP20 Version Top hat rail housing: grey Size W x H x D [mm]: 72 x 95 x 66.5 Material: plastic |
|  | ......................... Pc. .............................. € .............................. € Surface-mounted housing Housing for surface-mounted installation of top hat rail components such as power supplies or control units. With integrated 35 mm top hat rail for devices with a max. of 7 division units (18 mm). Technical data IP rating: IP 40 Cable routing surface-mounted or flush-mounted Version Size W x H x D [mm]: approx. 193 x 130 x 82 Colour: white Suitable for cascading Material: plastic |
|  | ......................... Pc. .............................. € .............................. € Building automation and control system for ventilation control incl. software application – natural night-time cooling Compact building automation and control system for control cabinet installation. Powerful building automation controller for standardized KNX communication protocol, configurable logic blocks (such as basic mathematical functions, shutter and blind control based on the position of the sun, temperature control). Functions Custom scenes can be created Up to 1,000 KNX group addresses-data points can be created per project Up to 62 users can be created in the user administration Visualisation function for PCs with Windows® operating system or mobile devices (iOS and Android, up to max. 10 devices at the same time) KNX interface function to be able to operate the ETS project remotely The visualisation interface allows for the display of all window statuses and room values Incl. natural ventilation software application KNX based ventilation regulation for motorised windows centrally within the building and individually for each room Individual activation of climate zones (up to 64 scenes) Timed ventilation Different times can be set for each climate zone, such as impact and continuous ventilation and flushing with fresh air. Night-time ventilation During non-occupied times to reduce energy consumption (of the activated cooling system). Indoor air quality Needs-based ventilation CO2-based, with adjustable threshold values. Central activation Central closing commands at set times and based on the weather for defined groups of windows. The user can override the regulation. User interface Different views can be set up on the user interface by room or by building. States for room conditions (CO2 and temperature values), statuses of window elements and if applicable shade systems and heaters Installation Mounted on DIN rail for control cabinet installation Technical data KNX Medium: TP256 Rated voltage: DC 24 to 30 V Power consumption: 4 W IP communication: Ethernet 10/100 BaseT (10/100 Mbit/s) Supported protocols: DHCP, AutoIP, TCP/IP, UDP/IP Connections IP: 2 x sockets RJ45 KNX: connection and branch terminal Ambient temperature: 0 °C to +45 °C Incl. device power supply, system housing for control cabinet installation and assembly accessories Planning service GEZE KNX ventilation control natural night-time cooling |
|  | ......................... Pc. .............................. € .............................. € IQ box KNX For connection of the window drives of the GEZE IQ windowdrive series to the KNX building system for intelligent natural ventilation. The IQ box KNX is compatible with the following GEZE window drives from software version 3.0: E 250 NT spindle drive Slimchain chain drive Powerchain chain drive Power lock locking drive F 1200+ Activation of the connected drives (position in %, speed in %) as well as feedback on the current position and window status (closed / open / opening /closing / position) is implemented by the KNX building bus. Ventilation functions gap ventilation and timed ventilation must be guaranteed without further controls. Technical data Supply voltage 24 V DC,+-25 %, SELV Max. current drives 6 A Induced current intake to KNX-bus 5 mA Induced current intake to 24 V 25 mA IP rating / protection class IP 20 protection class III Ambient temperature 5 °C .. +70 °C Connection cross-section 24 V & drive 1.5 mm² Connection cross-section push button 0.5 mm² Max. overall length of drive cable 15 m Dimensions of flush-mounted housing (UP) 50 mm x 45 mm x 19 mm Dimensions of top hat rail housing (HS) 98 mm x 62 mm x 18 mm (2 DU) Housing version ( ) Flush-mounted housing IQ Box KNX UP ( ) Top hat rail housing IQ-Box KNX HS |
|  | ......................... Pc. .............................. € .............................. € KNX power supply USB USB connection for bus access. Planning service GEZE KNX power supply |
|  | ......................... Pc. .............................. € .............................. € KNX bus line / area coupler Planning service GEZE KNX bus line/area coupler Properties Can be used as a line amplifier With integrated bus coupler With 2 yellow data traffic LEDs for higher and lower-level bus lines With green operating LED, red programming LED and red diagnostic LED With programming key and red programming LED bus connection via terminal Line connection via terminal |
|  | ......................... Pc. .............................. € .............................. € CO2 / temperature sensor climate zone The KNX Touch sensor measures the CO2 concentration, temperature and humidity in the room and calculates the dew point. The interior sensor can receive external values such as temperature, humidity and CO2 concentration via the bus and process them with its own data to obtain overall values (mixed values or room average). The KNX Touch has two touch push buttons that can be used to change the room temperature (target temperature), to switch between operating modes or as freely programmable bus buttons. Integrated PI controllers control the ventilation (according to CO2 concentration and humidity) and a heating/cooling system (according to the temperature). The integrated display shows the device’s own values and data received via the bus (such as the date and time). The housing has a frame for the switch series used in the building, allowing it to blend in seamlessly with the interior fittings. Note: frame on site Planning service GEZE CO2 / temperature sensor climate zone |
|  | ......................... Pc. .............................. € .............................. € KNX weather station Functions Brightness measurement (current light intensity) Wind measurement Precipitation detection Exterior temperature GPS receiver Sun position detection Shade detection Weekly and calendar timer Planning service GEZE KNX weather station |
|  | ......................... Pc. .............................. € .............................. € IQ box Safety HS TÜV-tested safety switching device for protection of the main and secondary closing edges of power-operated windows, hatches and skylights etc. in combination with safety edges and/or non-contact sensors. TÜV-certification in accordance with the Machinery Directive 2006/42/EC. One IQ box Safety is needed per window. If danger is detected by the sensors, the power-operated window stops or reverses the movement and prevents the risk of injury. Properties Fulfils the highest protection class specifications for power-operated windows according to the risk assessment performed in accordance with Machinery Directive 2006/42/EC (protection class 4) For natural ventilation (24V power supply, KNX, IQ gear) and/or smoke and heat extraction systems (SHEV control unit) DIP switch for (de)activating the sensor inputs. Adjustment to the parameters with ST 220 service terminal possible Top hat rail housing with plug-in terminals for easy wiring Integrated push button for closing windows manually during servicing Connection possibilities IQ box Safety is compatible with the GEZE IQ windowdrive window drives (24 V DC) from software version V3.2: E 250 NT spindle drive (also in smoke and heat extraction opening and locking systems) Slimchain chain drive Powerchain chain drive Power lock locking drive F1200+ from software version 1.0 Pre-set inputs for non-contact sensors, e.g. GC 339 or GC 342 Pre-set inputs for safety edges (terminating resistor from 4.5 k to 22 kOhm) Technical data Supply voltage 24 V DC, +-25 % Max. current drives 10 A Ambient temperature -5 °C…+70 °C Max. connection cross-section 2.5 mm² Max. length of the line to the drive 50 m Max. sensor line length see technical data of the respective sensor Dimensions of top hat rail casing (HxDxW) 90 mm x 60 mm x 35 mm (2 division units) Certification TÜV, EN ISO 13849-1:2016-06 und DIN EN ISO 134849-2:2013-02; Safety of machinery - Safety-related parts of control systems Note In accordance with Machinery Directive 2006/42/EC a risk assessment must be prepared for power-operated windows. The GEZE safety analysis for power-operated windows can serve as a guide for the risk analysis. These specifications determine the necessary protection class of the window and the definition of the protective measures. As the types of window and installation and the structural features of the buildings vary greatly, it is always advisable to undertake a feasibility study beforehand (especially in the case of retrofitting). |
|  | ......................... Pc. .............................. € .............................. € Sensors for protection (optional position) Safety edges and/or non-contact sensors for protection of the main and secondary closing edges on the window Definition of the window to be protected ( ) Inward opening ( ) Turn-and-tilt window ( ) Bottom-hung window ( ) Side-hung window other types of leaf available on request …………mm width …………mm height …………mm installation height …………mm opening width |
|  | ......................... Pc. .............................. € .............................. € GEZE GC 342 laser scanner (optional position) Self-monitored laser scanner to protect the main and secondary closing edges of the window. Technical data IP rating IP54 max. detection area 4 m (diagonal) Min. installation height 2500 mm Max. installation height 3870 mm Version ( ) outside ( ) inside ( ) stainless steel colour ( ) black ( ) white Protective cover to protect the laser scanner against interferences ( ) stainless steel colour ( ) black ( ) acc. to RAL and/or |
|  | ......................... Pc. .............................. € .............................. € GEZE GC 339 active infrared light curtain (optional position) Self-monitored light curtain to protect the main and secondary closing edges of the window. Technical data IP rating IP54 Detection area (for installation height 2.2 m) up to 2.2 x 0.35 m (W x D) 10 adjustable light curtain configurations Min. installation height 2000 mm Max. installation height 3000 mm Version ( ) outside ( ) inside Version ( ) stainless steel colour ( ) black ( ) white and/or |
|  | ......................... Pc. .............................. € .............................. € Safety edges (optional position) Safety edges to protect the main and secondary closing edges of the window. Terminating resistor between 4.5 k and 22 k Ohms for use with the IQ box Safety. Dimensions of the window ….. Number of safety edges per window ….. Length(s) of the safety edge(s) ….. |
|  | ......................... Pc. .............................. € .............................. € Delivery and installation Delivery, installation and commissioning by plant fitters or service partner. Safety analysis, instruction of the operator as to how the system works and handing over of the documentation. Annual maintenance and technical inspection by an expert authorised by the manufacturer incl. documentation of the inspection in an inspection book. |
|  | ......................... Pc. .............................. € .............................. € Project management service flat rate This item contains general project management work necessary to plan the system offered here. This includes planning and project management of the offered subsection. In addition, this item contains coordination work between the installation partner / planner and GEZE GmbH. Furthermore, it includes preparation of technical specifications which describe the version based on the coordination. Flat daily rate If in-person services are required for project management purposes, this will be calculated separately, plus travel expenses and per diem rates. |
|  | ......................... Pc. .............................. € .............................. € Natural night-time cooling climate zone control service Parameter setting for a climate zone according to the operator/planner specifications in accordance with the requirements specification Integration of the affected drives per climate zone Integration of the affected sensors per climate zone Creation of max. 3 scenes per climate zone (such as daytime regulation, night-time cooling, impact ventilation during break times) Additional scenes can be created for an additional fee (calculated according to actual work performed) |
|  | ......................... Pc. .............................. € .............................. € KNX parameter setting service KNX programming of KNX components delivered by GEZE GmbH according to previously agreed specifications of the planner / operator. Max. 100 KNX components IQ box KNX and max. 30 KNX sensors piece Including creation of documentation from ETS5 and including labelling KNX components (physic. address) |
|  | ......................... Pc. .............................. € .............................. € Data point transfer parameter setting service Gateway KNX -> BACnet on site KNX programming transfer of BMS data points max. 500 KNX data points |
|  | ......................... Pc. .............................. € .............................. € KNX ventilation control service Programming of ventilation control in consideration of interior and exterior values for temperature, CO2, wind, rain (max. 500 data points) |
|  | ......................... Pc. .............................. € .............................. € Housing pre-wiring service Pre-wiring of the housing per climate zone / room: Wiring of power supply with IQ box KNX, IQ box Safety or KNX switching actuator |
|  | ......................... Pc. .............................. € .............................. € On-site commissioning service Commissioning of KNX components (no installation, which must be completed on site in advance!). Commissioning of the GEZE natural night-time cooling application incl. setting the climate zones. Flat daily rate (xx) daily rates are suggested; calculated by actual work performed. |